## GENERAL
MODBUS TABLE ORGANIZATION
Starting Address of the Group Registers (Dec) | Starting Address of the Group Registers (Hex) | System Version (Release) | System Version (Build) | Group Name (Text) | Group Code (Hex) | Group Complexity (Hex) | Group Version (Hex)
768 | 300 |  |  | Device identifier
4096 | 1000 |  |  | Measures
4207 | 106F |  |  | Output Remote Command
4608 | 1200 |  |  | Settings
4688 | 1250 |  |  | Energies
4864 | 1300 |  |  | Average Measured values
5424 | 1530 |  |  | Average Measured values - Scaled
5504 | 1580 |  |  | Crest Factor
5632 | 1600 |  |  | Displacements
5664 | 1620 |  |  | Inputs
5888 | 1700 |  |  | Max. & Min.
8192 | 2000 |  |  | Standard Setup parameters (write 16 byte at once)
8704 | 2200 |  |  | Output option Setup parameters (write 24 byte at once)
28672 | 7000 |  |  | Harmonics
5888 | 1700 |  |  | Max. & Min.
MODBUS PROTOCOL DETAILS
Function Code (Dec) | Exception Codes (Dec) | Data Encoding
3 | 1, 2, 3 | "Big Endian" (most significant byte first)
16 | 1, 2, 3
MODBUS OVER SERIAL DETAILS
Physical Layer | Trasmission Modes | Device Addressing | Baud Rates (bit/s) | Data Bits | Data bits trasmission sequence | Parity | Stop Bits
standard EIA/TIA 485 (RS-485) two-wire configuration | RTU | 1÷247 | programmable | 8 | Least significant bit first | programmable | 1
MASTER/SLAVE COMMUNICATION TIMING
Timer Descrtiption | Timer Value (msec)
Inter-character time-out | Max. 20
Response delay (from master request) | 20÷300
Delay Time (between two master trasmissions) | < 20
REFER ALSO TO: | www.modbus.org | - MODBUS over serial line specification and implementation guide V1.02
- MODBUS APPLICATION PROTOCOL SPECIFICATION V1.1b
NOTE: | File and printed copies of this document are not subject to document change control.

## DISCRETE INPUT - Bits (R)
Register Number | Register Address (Dec) | Register Address (Hex) | Dimension [bit] | Description | Note | Read Function Codes (Dec) | Data Storing (2)
(no DISCRETE INPUTS availables)

## COILS - Bits (R&W)
Register Number | Register Address (Dec) | Register Address (Hex) | Dimension [bit] | Description | Note | Read Function Codes (Dec) | Write Function Codes (Dec) | Data Storing (2)
(no COILS availables)

## INPUT REGISTERS - Words (R)
Register Number | Register Address (Dec) | Register Address (Hex) | Dimension [word] | Bit Position | Description | Type | Scale | Unit | Range | Note | Read Function Code (Dec) | Data Storing (2)
769 | 768 | 300 | 1 |  | Device identifier
769 | 768 | 300 | 1 |  | Device identifier | unsigned integer | 0.01 | - |  | The device returns 0006h | 3
4097 | 4096 | 1000 | 124 |  | Measures
4097 | 4096 | 1000 | 2 |  | Phase 1 : phase voltage | unsigned integer | 1 | mV |  |  | 3
4099 | 4098 | 1002 | 2 |  | Phase 2 : phase voltage | unsigned integer | 1 | mV |  |  | 3
4101 | 4100 | 1004 | 2 |  | Phase 3 : phase voltage | unsigned integer | 1 | mV |  |  | 3
4103 | 4102 | 1006 | 2 |  | Phase 1 : current | unsigned integer | 1 | mA |  |  | 3
4105 | 4104 | 1008 | 2 |  | Phase 2 : current | unsigned integer | 1 | mA |  |  | 3
4107 | 4106 | 100A | 2 |  | Phase 3 : current | unsigned integer | 1 | mA |  |  | 3
4109 | 4108 | 100C | 2 |  | Neutral current | unsigned integer | 1 | mA |  |  | 3
4111 | 4110 | 100E | 2 |  | Chained voltage : L1-L2 | unsigned integer | 1 | mV |  |  | 3
4113 | 4112 | 1010 | 2 |  | Chained voltage : L2-L3 | unsigned integer | 1 | mV |  |  | 3
4115 | 4114 | 1012 | 2 |  | Chained voltage : L3-L1 | unsigned integer | 1 | mV |  |  | 3
4117 | 4116 | 1014 | 2 |  | 3-phase : active power | unsigned integer | 1, 0.01 | W |  | See Note 1 | 3
4119 | 4118 | 1016 | 2 |  | 3-phase : reactive power | unsigned integer | 1, 0.01 | var |  | See Note 1 | 3
4121 | 4120 | 1018 | 2 |  | 3-phase : apparent power | unsigned integer | 1, 0.01 | VA |  | See Note 1 | 3
4123 | 4122 | 101A | 1 |  | 3-phase : sign of active power | unsigned integer | 1 | - | 0, 1 | 0=positive, 1=negative | 3
4124 | 4123 | 101B | 1 |  | 3-phase : sign of reactive power | unsigned integer | 1 | - | 0, 1 | 0=positive, 1=negative | 3
4125 | 4124 | 101C | 2 |  | 3-phase : positive active energy | unsigned integer | 1, 10, 100, 1.000, 10.000, 100.000 | Wh |  | See Note 2 | 3 | Y
4127 | 4126 | 101E | 2 |  | 3-phase : positive reactive energy | unsigned integer | 1, 10, 100, 1.000, 10.000, 100.000 | varh |  | See Note 2 | 3 | Y
4129 | 4128 | 1020 | 2 |  | 3-phase : negative active energy | unsigned integer | 1, 10, 100, 1.000, 10.000, 100.000 | Wh |  | See Note 2 | 3 | Y
4131 | 4130 | 1022 | 2 |  | 3-phase : negative reactive energy | unsigned integer | 1, 10, 100, 1.000, 10.000, 100.000 | varh |  | See Note 2 | 3 | Y
4133 | 4132 | 1024 | 1 |  | 3-phase : power factor | signed integer | 0.01 | - |  |  | 3
4134 | 4133 | 1025 | 1 |  | 3-phase : sector of power factor (cap or ind) | unsigned integer | 1 | - | 0, 1, 2 | 0="PF=1", 1="ind" (L), 2="cap" (C) | 3
4135 | 4134 | 1026 | 1 |  | Frequency | unsigned integer | 0.1 | Hz |  |  | 3
4136 | 4135 | 1027 | 2 |  | 3-phase : average power | unsigned integer | 1, 0.01 | W |  | See Note 1 | 3
4138 | 4137 | 1029 | 2 |  | 3-phase : peak maximum demand | unsigned integer | 1, 0.01 | W |  | See Note 1 | 3 | Y
4140 | 4139 | 102B | 1 |  | Time counter for average power | unsigned integer | 1 | min |  |  | 3
4141 | 4140 | 102C | 2 |  | Phase 1 : active power | unsigned integer | 1, 0.01 | W |  | See Note 1 | 3
4143 | 4142 | 102E | 2 |  | Phase 2 : active power | unsigned integer | 1, 0.01 | W |  | See Note 1 | 3
4145 | 4144 | 1030 | 2 |  | Phase 3 : active power | unsigned integer | 1, 0.01 | W |  | See Note 1 | 3
4147 | 4146 | 1032 | 1 |  | Phase 1 : sign of active power | unsigned integer |  | - | 0, 1 | 0=positive, 1=negative | 3
4148 | 4147 | 1033 | 1 |  | Phase 2 : sign of active power | unsigned integer |  | - | 0, 1 | 0=positive, 1=negative | 3
4149 | 4148 | 1034 | 1 |  | Phase 3 : sign of active power | unsigned integer |  | - | 0, 1 | 0=positive, 1=negative | 3
4150 | 4149 | 1035 | 2 |  | Phase 1 : reactive power | unsigned integer | 1, 0.01 | var |  | See Note 1 | 3
4152 | 4151 | 1037 | 2 |  | Phase 2 : reactive power | unsigned integer | 1, 0.01 | var |  | See Note 1 | 3
4154 | 4153 | 1039 | 2 |  | Phase 3 : reactive power | unsigned integer | 1, 0.01 | var |  | See Note 1 | 3
4156 | 4155 | 103B | 1 |  | Phase 1 : sign of reactive power | unsigned integer |  | - | 0, 1 | 0=positive, 1=negative | 3
4157 | 4156 | 103C | 1 |  | Phase 2 : sign of reactive power | unsigned integer |  | - | 0, 1 | 0=positive, 1=negative | 3
4158 | 4157 | 103D | 1 |  | Phase 3 : sign of reactive power | unsigned integer |  | - | 0, 1 | 0=positive, 1=negative | 3
4159 | 4158 | 103E | 2 |  | Phase 1 : apparent power | unsigned integer | 1, 0.01 | VA |  | See Note 1 | 3
4161 | 4160 | 1040 | 2 |  | Phase 2 : apparent power | unsigned integer | 1, 0.01 | VA |  | See Note 1 | 3
4163 | 4162 | 1042 | 2 |  | Phase 3 : apparent power | unsigned integer | 1, 0.01 | VA |  | See Note 1 | 3
4165 | 4164 | 1044 | 1 |  | Phase 1 : power factor | signed integer | 0.01 | - |  |  | 3
4166 | 4165 | 1045 | 1 |  | Phase 2 : power factor | signed integer | 0.01 | - |  |  | 3
4167 | 4166 | 1046 | 1 |  | Phase 3 : power factor | signed integer | 0.01 | - |  |  | 3
4168 | 4167 | 1047 | 1 |  | Phase 1 : sector of power factor (cap or ind) | unsigned integer | 1 | - | 0, 1, 2 | 0="PF=1", 1="ind" (L), 2="cap" (C) | 3
4169 | 4168 | 1048 | 1 |  | Phase 2 : sector of power factor (cap or ind) | unsigned integer | 1 | - | 0, 1, 2 | 0="PF=1", 1="ind" (L), 2="cap" (C) | 3
4170 | 4169 | 1049 | 1 |  | Phase 3 : sector of power factor (cap or ind) | unsigned integer | 1 | - | 0, 1, 2 | 0="PF=1", 1="ind" (L), 2="cap" (C) | 3
4171 | 4170 | 104A | 1 |  | Phase 1 : THD V1 | unsigned integer | 0.1 | % |  | See Note 4 | 3
4172 | 4171 | 104B | 1 |  | Phase 2 : THD V2 | unsigned integer | 0.1 | % |  | See Note 4 | 3
4173 | 4172 | 104C | 1 |  | Phase 3 : THD V3 | unsigned integer | 0.1 | % |  | See Note 4 | 3
4174 | 4173 | 104D | 1 |  | Phase 1 : THD I1 | unsigned integer | 0.1 | % |  |  | 3
4175 | 4174 | 104E | 1 |  | Phase 2 : THD I2 | unsigned integer | 0.1 | % |  |  | 3
4176 | 4175 | 104F | 1 |  | Phase 3 : THD I3 | unsigned integer | 0.1 | % |  |  | 3
4177 | 4176 | 1050 | 2 |  | Phase 1 : I1 average | unsigned integer | 1 | mA |  |  | 3
4179 | 4178 | 1052 | 2 |  | Phase 2 : I2 average | unsigned integer | 1 | mA |  |  | 3
4181 | 4180 | 1054 | 2 |  | Phase 3 : I3 average | unsigned integer | 1 | mA |  |  | 3
4183 | 4182 | 1056 | 2 |  | Phase 1 : I1 peak Max. | unsigned integer | 1 | mA |  |  | 3
4185 | 4184 | 1058 | 2 |  | Phase 2 : I2 peak Max. | unsigned integer | 1 | mA |  |  | 3
4187 | 4186 | 105A | 2 |  | Phase 3 : I3 peak Max. | unsigned integer | 1 | mA |  |  | 3
4189 | 4188 | 105C | 2 |  | 3-phase : I average | unsigned integer | 1 | mA |  | (I1+I2+I3)/3 | 3
4191 | 4190 | 105E | 2 |  | Phase 1 : V1 min. | unsigned integer | 1 | mV |  | See Note 4 | 3
4193 | 4192 | 1060 | 2 |  | Phase 2 : V2 min. | unsigned integer | 1 | mV |  | See Note 4 | 3
4195 | 4194 | 1062 | 2 |  | Phase 3 : V3 min. | unsigned integer | 1 | mV |  | See Note 4 | 3
4197 | 4196 | 1064 | 2 |  | Phase 1 : V1 Max. | unsigned integer | 1 | mV |  | See Note 4 | 3
4199 | 4198 | 1066 | 2 |  | Phase 2 : V2 Max. | unsigned integer | 1 | mV |  | See Note 4 | 3
4201 | 4200 | 1068 | 2 |  | Phase 3 : V3 Max. | unsigned integer | 1 | mV |  | See Note 4 | 3
4203 | 4202 | 106A | 2 |  | 3-phase : partial active energy | unsigned integer | 1, 10, 100, 1000, 10.000, 100.000 | Wh |  | See Note 2 | 3
4205 | 4204 | 106C | 2 |  | 3-phase : partial reactive energy | unsigned integer | 1, 10, 100, 1000, 10.000, 100.000 | varh |  | See Note 2 | 3
4207 | 4206 | 106E | 1 |  | Operating timer counter | unsigned integer | 1 | h |  |  | 3
4208 | 4207 | 106F | 1 |  | Alarm status | unsigned integer | - | - | 0, 1 | 0: No active Alarm, 1: Alarm active | 3
4209 | 4208 | 1070 | 2 |  | 3-phase : average active power | unsigned integer | 1, 0.01 | W |  | See Note 1 | 3
4211 | 4210 | 1072 | 2 |  | 3-phase : average reactive power | unsigned integer | 1, 0.01 | var |  | See Note 1 | 3
4213 | 4212 | 1074 | 2 |  | 3-phase : average apparent power | unsigned integer | 1, 0.01 | VA |  | See Note 1 | 3
4215 | 4214 | 1076 | 2 |  | 3-phase : active PMD power | unsigned integer | 1, 0.01 | W |  | See Note 1 | 3
4217 | 4216 | 1078 | 2 |  | 3-phase : reactive PMD power | unsigned integer | 1, 0.01 | var |  | See Note 1 | 3
4219 | 4218 | 107A | 2 |  | 3-phase : apparent PMD power | unsigned integer | 1, 0.01 | VA |  | See Note 1 | 3
4609 | 4608 | 1200 | 7 |  | Settings
4609 | 4608 | 1200 | 1 |  | Current transformer ratio (CT) | unsigned integer | 1 | - |  |  | 3
4610 | 4609 | 1201 | 1 |  | Voltage transformer ratio (VT) | unsigned integer | 0.01 | - |  |  | 3
4611 | 4610 | 1202 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
4613 | 4612 | 1204 | 1 |  | RESERVED (returns 1007h) | [5 empty] | 3
4614 | 4613 | 1205 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
4615 | 4614 | 1206 | 1 |  | Digital Inputs Status | - | 1 | - |  | See Note 3 | 3
4689 | 4688 | 1250 | 16 |  | Energies
4689 | 4688 | 1250 | 2 |  | 3-phase : Positive total active energy | unsigned integer | 1, 10, 100, 1000, 10.000, 100.000 | Wh |  | See Note 2 | 3
4691 | 4690 | 1252 | 2 |  | 3-phase : Positive total reactive energy | unsigned integer | 1, 10, 100, 1000, 10.000, 100.000 | varh |  | See Note 2 | 3
4693 | 4692 | 1254 | 2 |  | 3-phase : Negative total active energy | unsigned integer | 1, 10, 100, 1000, 10.000, 100.000 | Wh |  | See Note 2 | 3
4695 | 4694 | 1256 | 2 |  | 3-phase : Negative total reactive energy | unsigned integer | 1, 10, 100, 1000, 10.000, 100.000 | varh |  | See Note 2 | 3
4697 | 4696 | 1258 | 2 |  | 3-phase Positive partial active energy or tariff 1 active energy (if option tariffs) | unsigned integer | 1, 10, 100, 1000, 10.000, 100.000 | Wh |  | See Note 2 | 3
4699 | 4698 | 125A | 2 |  | 3-phase Negative partial active energy or tariff 2 active energy (if option tariffs) | unsigned integer | 1, 10, 100, 1000, 10.000, 100.000 | Wh |  | See Note 2 | 3
4701 | 4700 | 125C | 2 |  | 3-phase Positive partial reactive energy or tariff 3 active energy (if option tariffs) | unsigned integer | 1, 10, 100, 1000, 10.000, 100.000 | Wh |  | See Note 2 | 3
4703 | 4702 | 125E | 2 |  | 3-phase Negative partial reactive energy or tariff 4 active energy (if option tariffs) | unsigned integer | 1, 10, 100, 1000, 10.000, 100.000 | varh |  | See Note 2 | 3
4865 | 4864 | 1300 | 30 |  | Average Measured values
4865 | 4864 | 1300 | 2 |  | 3-phase : active average power | unsigned integer | 1, 0.01 | W |  | See Note 1 | 3
4867 | 4866 | 1302 | 2 |  | 3-phase : reactive average power | unsigned integer | 1, 0.01 | var |  | See Note 1 | 3
4869 | 4868 | 1304 | 2 |  | 3-phase : apparent average power | unsigned integer | 1, 0.01 | VA |  | See Note 1 | 3
4871 | 4870 | 1306 | 2 |  | 3-phase : active average power tarifs 1 | unsigned integer | 1, 0.01 | W |  | See Note 1 | 3
4873 | 4872 | 1308 | 2 |  | 3-phase : reactive average power tarifs 1 | unsigned integer | 1, 0.01 | var |  | See Note 1 | 3
4875 | 4874 | 130A | 2 |  | 3-phase : apparent average power tarifs 1 | unsigned integer | 1, 0.01 | VA |  | See Note 1 | 3
4877 | 4876 | 130C | 2 |  | 3-phase : active average power tarifs 2 | unsigned integer | 1, 0.01 | W |  | See Note 1 | 3
4879 | 4878 | 130E | 2 |  | 3-phase : reactive average power tarifs 2 | unsigned integer | 1, 0.01 | var |  | See Note 1 | 3
4881 | 4880 | 1310 | 2 |  | 3-phase : apparent average power tarifs 2 | unsigned integer | 1, 0.01 | VA |  | See Note 1 | 3
4883 | 4882 | 1312 | 2 |  | 3-phase : active average power tarifs 3 | unsigned integer | 1, 0.01 | W |  | See Note 1 | 3
4885 | 4884 | 1314 | 2 |  | 3-phase : reactive average power tarifs 3 | unsigned integer | 1, 0.01 | var |  | See Note 1 | 3
4887 | 4886 | 1316 | 2 |  | 3-phase : apparent average power tarifs 3 | unsigned integer | 1, 0.01 | VA |  | See Note 1 | 3
4889 | 4888 | 1318 | 2 |  | 3-phase : active average power tarifs 4 | unsigned integer | 1, 0.01 | W |  | See Note 1 | 3
4891 | 4890 | 131A | 2 |  | 3-phase : reactive average power tarifs 4 | unsigned integer | 1, 0.01 | var |  | See Note 1 | 3
4893 | 4892 | 131C | 2 |  | 3-phase : apparent average power tarifs 4 | unsigned integer | 1, 0.01 | VA |  | See Note 1 | 3
5425 | 5424 | 1530 | 14 |  | Average Measured values - Scaled
5425 | 5424 | 1530 | 2 |  | Total Apparent power | unsigned integer | 1 | VA |  |  | 3
5427 | 5426 | 1532 | 2 |  | 3-phase : average active power | unsigned integer | 1 | W |  |  | 3
5429 | 5428 | 1534 | 2 |  | 3-phase : average reactive power | unsigned integer | 1 | var |  |  | 3
5431 | 5430 | 1536 | 2 |  | 3-phase : average apparent power | unsigned integer | 1 | VA |  |  | 3
5433 | 5432 | 1538 | 2 |  | 3-phase : max active power | unsigned integer | 1 | W |  |  | 3
5435 | 5434 | 153A | 2 |  | 3-phase : max reactive power | unsigned integer | 1 | var |  |  | 3
5437 | 5436 | 153C | 2 |  | 3-phase : max apparent power | unsigned integer | 1 | VA |  |  | 3
5505 | 5504 | 1580 | 9 |  | Crest Factor
5505 | 5504 | 1580 | 1 |  | Phase1 voltage crest factor | unsigned integer | 0.001 | - |  |  | 3
5506 | 5505 | 1581 | 1 |  | Phase2 voltage crest factor | unsigned integer | 0.001 | - |  |  | 3
5507 | 5506 | 1582 | 1 |  | Phase3 voltage crest factor | unsigned integer | 0.001 | - |  |  | 3
5508 | 5507 | 1583 | 1 |  | Phase1 current crest factor | unsigned integer | 0.001 | - |  |  | 3
5509 | 5508 | 1584 | 1 |  | Phase2 current crest factor | unsigned integer | 0.001 | - |  |  | 3
5510 | 5509 | 1585 | 1 |  | Phase3 current crest factor | unsigned integer | 0.001 | - |  |  | 3
5511 | 5510 | 1586 | 1 |  | Phase1-2 voltage crest factor | unsigned integer | 0.001 | - |  |  | 3
5512 | 5511 | 1587 | 1 |  | Phase2-3 voltage crest factor | unsigned integer | 0.001 | - |  |  | 3
5513 | 5512 | 1588 | 1 |  | Phase3-1 voltage crest factor | unsigned integer | 0.001 | - |  |  | 3
5633 | 5632 | 1600 | 10 |  | Displacements
5633 | 5632 | 1600 | 1 |  | phase displacement V1-V2 (V12-V23) | unsigned integer | 0.1 | ° |  | See Note 4 | 3
5634 | 5633 | 1601 | 1 |  | phase displacement V2-V3 (V23-V31) | unsigned integer | 0.1 | ° |  | See Note 4 | 3
5635 | 5634 | 1602 | 1 |  | phase displacement V3-V1 (V31-V12) | unsigned integer | 0.1 | ° |  | See Note 4 | 3
5636 | 5635 | 1603 | 1 |  | phase displacement I1-I2 | unsigned integer | 0.1 | ° |  |  | 3
5637 | 5636 | 1604 | 1 |  | phase displacement I2-I3 | unsigned integer | 0.1 | ° |  |  | 3
5638 | 5637 | 1605 | 1 |  | phase displacement I3-I1 | unsigned integer | 0.1 | ° |  |  | 3
5639 | 5638 | 1606 | 1 |  | phase displacement V1-I1 | unsigned integer | 0.1 | ° |  |  | 3
5640 | 5639 | 1607 | 1 |  | phase displacement V2-I2 | unsigned integer | 0.1 | ° |  |  | 3
5641 | 5640 | 1608 | 1 |  | phase displacement V3-I3 | unsigned integer | 0.1 | ° |  |  | 3
5642 | 5641 | 1609 | 1 |  | phase displacement total | unsigned integer | 0.1 | ° |  |  | 3
5665 | 5664 | 1620 | 12 |  | Inputs
5665 | 5664 | 1620 | 2 |  | Counting input 1 | unsigned integer | - | - |  |  | 3
5667 | 5666 | 1622 | 2 |  | Counting input 2 | unsigned integer | - | - |  |  | 3
5669 | 5668 | 1624 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
5671 | 5670 | 1626 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
5673 | 5672 | 1628 | 1 |  | Input 1 state | unsigned integer | - | - | 0, 1 | 0: Open, 1: Close | 3
5674 | 5673 | 1629 | 1 |  | Input 2 state | unsigned integer | - | - | 0, 1 | 0: Open, 1: Close | 3
5675 | 5674 | 162A | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
5676 | 5675 | 162B | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
5889 | 5888 | 1700 | 56 |  | Max. & Min.
5889 | 5888 | 1700 | 2 |  | Low Positive Active Energy | unsigned integer | 1 | Wh |  |  | 3
5891 | 5890 | 1702 | 2 |  | High Positive Active Energy | unsigned integer | 1 | MWh |  |  | 3
5893 | 5892 | 1704 | 2 |  | Low Positive Reactive Energy | unsigned integer | 1 | varh |  |  | 3
5895 | 5894 | 1706 | 2 |  | High Positive Reactive Energy | unsigned integer | 1 | Mvarh |  |  | 3
5897 | 5896 | 1708 | 2 |  | Low Negative Active Energy | unsigned integer | 1 | Wh |  |  | 3
5899 | 5898 | 170A | 2 |  | High Negative Active Energy | unsigned integer | 1 | MWh |  |  | 3
5901 | 5900 | 170C | 2 |  | Low Negative Reactive Energy | unsigned integer | 1 | varh |  |  | 3
5903 | 5902 | 170E | 2 |  | High Negative Reactive Energy | unsigned integer | 1 | Mvarh |  |  | 3
5905 | 5904 | 1710 | 2 |  | Low Partial Active Energy | unsigned integer | 1 | Wh |  |  | 3
5907 | 5906 | 1712 | 2 |  | High Partial Active Energy | unsigned integer | 1 | MWh |  |  | 3
5909 | 5908 | 1714 | 2 |  | Low Partial Reactive Energy | unsigned integer | 1 | varh |  |  | 3
5911 | 5910 | 1716 | 2 |  | High Partial Reactive Energy | unsigned integer | 1 | Mvarh |  |  | 3
5913 | 5912 | 1718 | 2 |  | Low Negative Partial Active Energy | unsigned integer | 1 | Wh |  |  | 3
5915 | 5914 | 171A | 2 |  | High Negative Partial Active Energy | unsigned integer | 1 | MWh |  |  | 3
5917 | 5916 | 171C | 2 |  | Low Negative Partial Reactive Energy | unsigned integer | 1 | varh |  |  | 3
5919 | 5918 | 171E | 2 |  | High Negative Partial Reactive Energy | unsigned integer | 1 | Mvarh |  |  | 3
5921 | 5920 | 1720 | 2 |  | Signed Total active power | signed integer | 1 | W |  |  | 3
5923 | 5922 | 1722 | 2 |  | Signed Total reactive power | signed integer | 1 | var |  |  | 3
5925 | 5924 | 1724 | 2 |  | Signed phase1 active power | signed integer | 1 | W |  |  | 3
5927 | 5926 | 1726 | 2 |  | Signed phase2 active power | signed integer | 1 | W |  |  | 3
5929 | 5928 | 1728 | 2 |  | Signed phase3 active power | signed integer | 1 | W |  |  | 3
5931 | 5930 | 172A | 2 |  | Signed phase1 reactive power | signed integer | 1 | Var |  |  | 3
5933 | 5932 | 172C | 2 |  | Signed phase2 reactive power | signed integer | 1 | Var |  |  | 3
5935 | 5934 | 172E | 2 |  | Signed phase3 reactive power | signed integer | 1 | var |  |  | 3
5937 | 5936 | 1730 | 2 |  | Signed total Power Factor | signed integer | 0.001 | - |  |  | 3
5939 | 5938 | 1732 | 2 |  | Signed phase1 Power Factor | signed integer | 0.001 | - |  |  | 3
5941 | 5940 | 1734 | 2 |  | Signed phase2 Power Factor | signed integer | 0.001 | - |  |  | 3
5943 | 5942 | 1736 | 2 |  | Signed phase3 Power Factor | signed integer | 0.001 | - |  |  | 3
28673 | 28672 | 7000 | 200 |  | Harmonics
28673 | 28672 | 7000 | 1 |  | Current phase 1 - fundamental | unsigned integer | 0.1 | % |  |  | 3
28674 | 28673 | 7001 | 1 |  | Current phase 1 - 2nd harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28675 | 28674 | 7002 | 1 |  | Current phase 1 - 3rd harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28676 | 28675 | 7003 | 1 |  | Current phase 1 - 4th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28677 | 28676 | 7004 | 1 |  | Current phase 1 - 5th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28678 | 28677 | 7005 | 1 |  | Current phase 1 - 6th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28679 | 28678 | 7006 | 1 |  | Current phase 1 - 7th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28680 | 28679 | 7007 | 1 |  | Current phase 1 - 8th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28681 | 28680 | 7008 | 1 |  | Current phase 1 - 9th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28682 | 28681 | 7009 | 1 |  | Current phase 1 - 10th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28683 | 28682 | 700A | 1 |  | Current phase 1 - 11th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28684 | 28683 | 700B | 1 |  | Current phase 1 - 12th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28685 | 28684 | 700C | 1 |  | Current phase 1 - 13th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28686 | 28685 | 700D | 1 |  | Current phase 1 - 14th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28687 | 28686 | 700E | 1 |  | Current phase 1 - 15th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28688 | 28687 | 700F | 1 |  | Current phase 1 - 16th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28689 | 28688 | 7010 | 1 |  | Current phase 1 - 17th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28690 | 28689 | 7011 | 1 |  | Current phase 1 - 18th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28691 | 28690 | 7012 | 1 |  | Current phase 1 - 19th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28692 | 28691 | 7013 | 1 |  | Current phase 1 - 20th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28693 | 28692 | 7014 | 1 |  | Current phase 1 - 21st harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28694 | 28693 | 7015 | 1 |  | Current phase 1 - 22nd harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28695 | 28694 | 7016 | 1 |  | Current phase 1 - 23rd harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28696 | 28695 | 7017 | 1 |  | Current phase 1 - 24th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28697 | 28696 | 7018 | 1 |  | Current phase 1 - 25th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28698 | 28697 | 7019 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28699 | 28698 | 701A | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28700 | 28699 | 701B | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28701 | 28700 | 701C | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28702 | 28701 | 701D | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28703 | 28702 | 701E | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28704 | 28703 | 701F | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28705 | 28704 | 7020 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28706 | 28705 | 7021 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28707 | 28706 | 7022 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28708 | 28707 | 7023 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28709 | 28708 | 7024 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28710 | 28709 | 7025 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28711 | 28710 | 7026 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28712 | 28711 | 7027 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28713 | 28712 | 7028 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28714 | 28713 | 7029 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28715 | 28714 | 702A | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28716 | 28715 | 702B | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28717 | 28716 | 702C | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28718 | 28717 | 702D | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28719 | 28718 | 702E | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28720 | 28719 | 702F | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28721 | 28720 | 7030 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28722 | 28721 | 7031 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28737 | 28736 | 7040 | 1 |  | Current phase 2 - fundamental | unsigned integer | 0.1 | % |  |  | 3
28738 | 28737 | 7041 | 1 |  | Current phase 2 - 2nd harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28739 | 28738 | 7042 | 1 |  | Current phase 2 - 3rd harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28740 | 28739 | 7043 | 1 |  | Current phase 2 - 4th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28741 | 28740 | 7044 | 1 |  | Current phase 2 - 5th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28742 | 28741 | 7045 | 1 |  | Current phase 2 - 6th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28743 | 28742 | 7046 | 1 |  | Current phase 2 - 7th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28744 | 28743 | 7047 | 1 |  | Current phase 2 - 8th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28745 | 28744 | 7048 | 1 |  | Current phase 2 - 9th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28746 | 28745 | 7049 | 1 |  | Current phase 2 - 10th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28747 | 28746 | 704A | 1 |  | Current phase 2 - 11th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28748 | 28747 | 704B | 1 |  | Current phase 2 - 12th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28749 | 28748 | 704C | 1 |  | Current phase 2 - 13th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28750 | 28749 | 704D | 1 |  | Current phase 2 - 14th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28751 | 28750 | 704E | 1 |  | Current phase 2 - 15th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28752 | 28751 | 704F | 1 |  | Current phase 2 - 16th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28753 | 28752 | 7050 | 1 |  | Current phase 2 - 17th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28754 | 28753 | 7051 | 1 |  | Current phase 2 - 18th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28755 | 28754 | 7052 | 1 |  | Current phase 2 - 19th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28756 | 28755 | 7053 | 1 |  | Current phase 2 - 20th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28757 | 28756 | 7054 | 1 |  | Current phase 2 - 21st harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28758 | 28757 | 7055 | 1 |  | Current phase 2 - 22nd harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28759 | 28758 | 7056 | 1 |  | Current phase 2 - 23rd harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28760 | 28759 | 7057 | 1 |  | Current phase 2 - 24th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28761 | 28760 | 7058 | 1 |  | Current phase 2 - 25th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28762 | 28761 | 7059 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28763 | 28762 | 705A | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28764 | 28763 | 705B | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28765 | 28764 | 705C | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28766 | 28765 | 705D | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28767 | 28766 | 705E | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28768 | 28767 | 705F | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28769 | 28768 | 7060 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28770 | 28769 | 7061 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28771 | 28770 | 7062 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28772 | 28771 | 7063 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28773 | 28772 | 7064 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28774 | 28773 | 7065 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28775 | 28774 | 7066 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28776 | 28775 | 7067 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28777 | 28776 | 7068 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28778 | 28777 | 7069 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28779 | 28778 | 706A | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28780 | 28779 | 706B | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28781 | 28780 | 706C | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28782 | 28781 | 706D | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28783 | 28782 | 706E | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28784 | 28783 | 706F | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28785 | 28784 | 7070 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28786 | 28785 | 7071 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28801 | 28800 | 7080 | 1 |  | Current phase 3 - fundamental | unsigned integer | 0.1 | % |  |  | 3
28802 | 28801 | 7081 | 1 |  | Current phase 3 - 2nd harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28803 | 28802 | 7082 | 1 |  | Current phase 3 - 3rd harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28804 | 28803 | 7083 | 1 |  | Current phase 3 - 4th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28805 | 28804 | 7084 | 1 |  | Current phase 3 - 5th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28806 | 28805 | 7085 | 1 |  | Current phase 3 - 6th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28807 | 28806 | 7086 | 1 |  | Current phase 3 - 7th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28808 | 28807 | 7087 | 1 |  | Current phase 3 - 8th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28809 | 28808 | 7088 | 1 |  | Current phase 3 - 9th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28810 | 28809 | 7089 | 1 |  | Current phase 3 - 10th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28811 | 28810 | 708A | 1 |  | Current phase 3 - 11th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28812 | 28811 | 708B | 1 |  | Current phase 3 - 12th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28813 | 28812 | 708C | 1 |  | Current phase 3 - 13th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28814 | 28813 | 708D | 1 |  | Current phase 3 - 14th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28815 | 28814 | 708E | 1 |  | Current phase 3 - 15th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28816 | 28815 | 708F | 1 |  | Current phase 3 - 16th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28817 | 28816 | 7090 | 1 |  | Current phase 3 - 17th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28818 | 28817 | 7091 | 1 |  | Current phase 3 - 18th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28819 | 28818 | 7092 | 1 |  | Current phase 3 - 19th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28820 | 28819 | 7093 | 1 |  | Current phase 3 - 20th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28821 | 28820 | 7094 | 1 |  | Current phase 3 - 21st harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28822 | 28821 | 7095 | 1 |  | Current phase 3 - 22nd harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28823 | 28822 | 7096 | 1 |  | Current phase 3 - 23rd harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28824 | 28823 | 7097 | 1 |  | Current phase 3 - 24th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28825 | 28824 | 7098 | 1 |  | Current phase 3 - 25th harmonic percentage | unsigned integer | 0.1 | % |  |  | 3
28826 | 28825 | 7099 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28827 | 28826 | 709A | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28828 | 28827 | 709B | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28829 | 28828 | 709C | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28830 | 28829 | 709D | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28831 | 28830 | 709E | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28832 | 28831 | 709F | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28833 | 28832 | 70A0 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28834 | 28833 | 70A1 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28835 | 28834 | 70A2 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28836 | 28835 | 70A3 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28837 | 28836 | 70A4 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28838 | 28837 | 70A5 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28839 | 28838 | 70A6 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28840 | 28839 | 70A7 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28841 | 28840 | 70A8 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28842 | 28841 | 70A9 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28843 | 28842 | 70AA | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28844 | 28843 | 70AB | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28845 | 28844 | 70AC | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28846 | 28845 | 70AD | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28847 | 28846 | 70AE | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28848 | 28847 | 70AF | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28849 | 28848 | 70B0 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28850 | 28849 | 70B1 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28865 | 28864 | 70C0 | 1 |  | Voltage phase 1 - fundamental | unsigned integer | 0.1 | % |  | See Note 4 | 3
28866 | 28865 | 70C1 | 1 |  | Voltage phase 1 - 2nd harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28867 | 28866 | 70C2 | 1 |  | Voltage phase 1 - 3rd harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28868 | 28867 | 70C3 | 1 |  | Voltage phase 1 - 4th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28869 | 28868 | 70C4 | 1 |  | Voltage phase 1 - 5th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28870 | 28869 | 70C5 | 1 |  | Voltage phase 1 - 6th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28871 | 28870 | 70C6 | 1 |  | Voltage phase 1 - 7th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28872 | 28871 | 70C7 | 1 |  | Voltage phase 1 - 8th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28873 | 28872 | 70C8 | 1 |  | Voltage phase 1 - 9th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28874 | 28873 | 70C9 | 1 |  | Voltage phase 1 - 10th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28875 | 28874 | 70CA | 1 |  | Voltage phase 1 - 11th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28876 | 28875 | 70CB | 1 |  | Voltage phase 1 - 12th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28877 | 28876 | 70CC | 1 |  | Voltage phase 1 - 13th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28878 | 28877 | 70CD | 1 |  | Voltage phase 1 - 14th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28879 | 28878 | 70CE | 1 |  | Voltage phase 1 - 15th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28880 | 28879 | 70CF | 1 |  | Voltage phase 1 - 16th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28881 | 28880 | 70D0 | 1 |  | Voltage phase 1 - 17th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28882 | 28881 | 70D1 | 1 |  | Voltage phase 1 - 18th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28883 | 28882 | 70D2 | 1 |  | Voltage phase 1 - 19th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28884 | 28883 | 70D3 | 1 |  | Voltage phase 1 - 20th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28885 | 28884 | 70D4 | 1 |  | Voltage phase 1 - 21st harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28886 | 28885 | 70D5 | 1 |  | Voltage phase 1 - 22nd harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28887 | 28886 | 70D6 | 1 |  | Voltage phase 1 - 23rd harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28888 | 28887 | 70D7 | 1 |  | Voltage phase 1 - 24th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28889 | 28888 | 70D8 | 1 |  | Voltage phase 1 - 25th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28890 | 28889 | 70D9 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28891 | 28890 | 70DA | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28892 | 28891 | 70DB | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28893 | 28892 | 70DC | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28894 | 28893 | 70DD | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28895 | 28894 | 70DE | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28896 | 28895 | 70DF | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28897 | 28896 | 70E0 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28898 | 28897 | 70E1 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28899 | 28898 | 70E2 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28900 | 28899 | 70E3 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28901 | 28900 | 70E4 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28902 | 28901 | 70E5 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28903 | 28902 | 70E6 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28904 | 28903 | 70E7 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28905 | 28904 | 70E8 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28906 | 28905 | 70E9 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28907 | 28906 | 70EA | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28908 | 28907 | 70EB | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28909 | 28908 | 70EC | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28910 | 28909 | 70ED | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28911 | 28910 | 70EE | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28912 | 28911 | 70EF | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28913 | 28912 | 70F0 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28914 | 28913 | 70F1 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28929 | 28928 | 7100 | 100
28929 | 28928 | 7100 | 1 |  | Voltage phase 2 - fundamental | unsigned integer | 0.1 | % |  | See Note 4 | 3
28930 | 28929 | 7101 | 1 |  | Voltage phase 2 - 2nd harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28931 | 28930 | 7102 | 1 |  | Voltage phase 2 - 3rd harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28932 | 28931 | 7103 | 1 |  | Voltage phase 2 - 4th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28933 | 28932 | 7104 | 1 |  | Voltage phase 2 - 5th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28934 | 28933 | 7105 | 1 |  | Voltage phase 2 - 6th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28935 | 28934 | 7106 | 1 |  | Voltage phase 2 - 7th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28936 | 28935 | 7107 | 1 |  | Voltage phase 2 - 8th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28937 | 28936 | 7108 | 1 |  | Voltage phase 2 - 9th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28938 | 28937 | 7109 | 1 |  | Voltage phase 2 - 10th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28939 | 28938 | 710A | 1 |  | Voltage phase 2 - 11th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28940 | 28939 | 710B | 1 |  | Voltage phase 2 - 12th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28941 | 28940 | 710C | 1 |  | Voltage phase 2 - 13th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28942 | 28941 | 710D | 1 |  | Voltage phase 2 - 14th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28943 | 28942 | 710E | 1 |  | Voltage phase 2 - 15th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28944 | 28943 | 710F | 1 |  | Voltage phase 2 - 16th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28945 | 28944 | 7110 | 1 |  | Voltage phase 2 - 17th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28946 | 28945 | 7111 | 1 |  | Voltage phase 2 - 18th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28947 | 28946 | 7112 | 1 |  | Voltage phase 2 - 19th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28948 | 28947 | 7113 | 1 |  | Voltage phase 2 - 20th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28949 | 28948 | 7114 | 1 |  | Voltage phase 2 - 21st harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28950 | 28949 | 7115 | 1 |  | Voltage phase 2 - 22nd harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28951 | 28950 | 7116 | 1 |  | Voltage phase 2 - 23rd harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28952 | 28951 | 7117 | 1 |  | Voltage phase 2 - 24th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28953 | 28952 | 7118 | 1 |  | Voltage phase 2 - 25th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28954 | 28953 | 7119 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28955 | 28954 | 711A | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28956 | 28955 | 711B | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28957 | 28956 | 711C | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28958 | 28957 | 711D | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28959 | 28958 | 711E | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28960 | 28959 | 711F | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28961 | 28960 | 7120 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28962 | 28961 | 7121 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28963 | 28962 | 7122 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28964 | 28963 | 7123 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28965 | 28964 | 7124 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28966 | 28965 | 7125 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28967 | 28966 | 7126 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28968 | 28967 | 7127 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28969 | 28968 | 7128 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28970 | 28969 | 7129 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28971 | 28970 | 712A | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28972 | 28971 | 712B | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28973 | 28972 | 712C | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28974 | 28973 | 712D | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28975 | 28974 | 712E | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28976 | 28975 | 712F | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28977 | 28976 | 7130 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28978 | 28977 | 7131 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
28993 | 28992 | 7140 | 1 |  | Voltage phase 3 - fundamental | unsigned integer | 0.1 | % |  | See Note 4 | 3
28994 | 28993 | 7141 | 1 |  | Voltage phase 3 - 2nd harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28995 | 28994 | 7142 | 1 |  | Voltage phase 3 - 3rd harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28996 | 28995 | 7143 | 1 |  | Voltage phase 3 - 4th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28997 | 28996 | 7144 | 1 |  | Voltage phase 3 - 5th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28998 | 28997 | 7145 | 1 |  | Voltage phase 3 - 6th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
28999 | 28998 | 7146 | 1 |  | Voltage phase 3 - 7th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29000 | 28999 | 7147 | 1 |  | Voltage phase 3 - 8th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29001 | 29000 | 7148 | 1 |  | Voltage phase 3 - 9th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29002 | 29001 | 7149 | 1 |  | Voltage phase 3 - 10th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29003 | 29002 | 714A | 1 |  | Voltage phase 3 - 11th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29004 | 29003 | 714B | 1 |  | Voltage phase 3 - 12th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29005 | 29004 | 714C | 1 |  | Voltage phase 3 - 13th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29006 | 29005 | 714D | 1 |  | Voltage phase 3 - 14th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29007 | 29006 | 714E | 1 |  | Voltage phase 3 - 15th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29008 | 29007 | 714F | 1 |  | Voltage phase 3 - 16th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29009 | 29008 | 7150 | 1 |  | Voltage phase 3 - 17th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29010 | 29009 | 7151 | 1 |  | Voltage phase 3 - 18th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29011 | 29010 | 7152 | 1 |  | Voltage phase 3 - 19th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29012 | 29011 | 7153 | 1 |  | Voltage phase 3 - 20th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29013 | 29012 | 7154 | 1 |  | Voltage phase 3 - 21st harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29014 | 29013 | 7155 | 1 |  | Voltage phase 3 - 22nd harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29015 | 29014 | 7156 | 1 |  | Voltage phase 3 - 23rd harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29016 | 29015 | 7157 | 1 |  | Voltage phase 3 - 24th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29017 | 29016 | 7158 | 1 |  | Voltage phase 3 - 25th harmonic percentage | unsigned integer | 0.1 | % |  | See Note 4 | 3
29018 | 29017 | 7159 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29019 | 29018 | 715A | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29020 | 29019 | 715B | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29021 | 29020 | 715C | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29022 | 29021 | 715D | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29023 | 29022 | 715E | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29024 | 29023 | 715F | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29025 | 29024 | 7160 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29026 | 29025 | 7161 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29027 | 29026 | 7162 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29028 | 29027 | 7163 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29029 | 29028 | 7164 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29030 | 29029 | 7165 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29031 | 29030 | 7166 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29032 | 29031 | 7167 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29033 | 29032 | 7168 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29034 | 29033 | 7169 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29035 | 29034 | 716A | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29036 | 29035 | 716B | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29037 | 29036 | 716C | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29038 | 29037 | 716D | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29039 | 29038 | 716E | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29040 | 29039 | 716F | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29041 | 29040 | 7170 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29042 | 29041 | 7171 | 1 |  | RESERVED (returns 0000h) | [5 empty] | 3
29185 | 29184 | 7200 | 200
29185 | 29184 | 7200 | 2 |  | Current phase 1 - 1st harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29187 | 29186 | 7202 | 2 |  | Current phase 1 - 2nd harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29189 | 29188 | 7204 | 2 |  | Current phase 1 - 3rd harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29191 | 29190 | 7206 | 2 |  | Current phase 1 - 4th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29193 | 29192 | 7208 | 2 |  | Current phase 1 - 5th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29195 | 29194 | 720A | 2 |  | Current phase 1 - 6th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29197 | 29196 | 720C | 2 |  | Current phase 1 - 7th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29199 | 29198 | 720E | 2 |  | Current phase 1 - 8th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29201 | 29200 | 7210 | 2 |  | Current phase 1 - 9th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29203 | 29202 | 7212 | 2 |  | Current phase 1 - 10th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29205 | 29204 | 7214 | 2 |  | Current phase 1 - 11th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29207 | 29206 | 7216 | 2 |  | Current phase 1 - 12th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29209 | 29208 | 7218 | 2 |  | Current phase 1 - 13th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29211 | 29210 | 721A | 2 |  | Current phase 1 - 14th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29213 | 29212 | 721C | 2 |  | Current phase 1 - 15th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29215 | 29214 | 721E | 2 |  | Current phase 1 - 16th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29217 | 29216 | 7220 | 2 |  | Current phase 1 - 17th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29219 | 29218 | 7222 | 2 |  | Current phase 1 - 18th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29221 | 29220 | 7224 | 2 |  | Current phase 1 - 19th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29223 | 29222 | 7226 | 2 |  | Current phase 1 - 20th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29225 | 29224 | 7228 | 2 |  | Current phase 1 - 21st harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29227 | 29226 | 722A | 2 |  | Current phase 1 - 22nd harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29229 | 29228 | 722C | 2 |  | Current phase 1 - 23rd harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29231 | 29230 | 722E | 2 |  | Current phase 1 - 24th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29233 | 29232 | 7230 | 2 |  | Current phase 1 - 25th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29235 | 29234 | 7232 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29237 | 29236 | 7234 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29239 | 29238 | 7236 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29241 | 29240 | 7238 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29243 | 29242 | 723A | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29245 | 29244 | 723C | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29247 | 29246 | 723E | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29249 | 29248 | 7240 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29251 | 29250 | 7242 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29253 | 29252 | 7244 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29255 | 29254 | 7246 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29257 | 29256 | 7248 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29259 | 29258 | 724A | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29261 | 29260 | 724C | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29263 | 29262 | 724E | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29265 | 29264 | 7250 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29267 | 29266 | 7252 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29269 | 29268 | 7254 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29271 | 29270 | 7256 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29273 | 29272 | 7258 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29275 | 29274 | 725A | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29277 | 29276 | 725C | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29279 | 29278 | 725E | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29281 | 29280 | 7260 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29283 | 29282 | 7262 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29313 | 29312 | 7280 | 2 |  | Current phase 2 - 1st harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29315 | 29314 | 7282 | 2 |  | Current phase 2 - 2nd harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29317 | 29316 | 7284 | 2 |  | Current phase 2 - 3rd harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29319 | 29318 | 7286 | 2 |  | Current phase 2 - 4th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29321 | 29320 | 7288 | 2 |  | Current phase 2 - 5th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29323 | 29322 | 728A | 2 |  | Current phase 2 - 6th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29325 | 29324 | 728C | 2 |  | Current phase 2 - 7th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29327 | 29326 | 728E | 2 |  | Current phase 2 - 8th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29329 | 29328 | 7290 | 2 |  | Current phase 2 - 9th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29331 | 29330 | 7292 | 2 |  | Current phase 2 - 10th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29333 | 29332 | 7294 | 2 |  | Current phase 2 - 11th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29335 | 29334 | 7296 | 2 |  | Current phase 2 - 12th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29337 | 29336 | 7298 | 2 |  | Current phase 2 - 13th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29339 | 29338 | 729A | 2 |  | Current phase 2 - 14th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29341 | 29340 | 729C | 2 |  | Current phase 2 - 15th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29343 | 29342 | 729E | 2 |  | Current phase 2 - 16th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29345 | 29344 | 72A0 | 2 |  | Current phase 2 - 17th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29347 | 29346 | 72A2 | 2 |  | Current phase 2 - 18th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29349 | 29348 | 72A4 | 2 |  | Current phase 2 - 19th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29351 | 29350 | 72A6 | 2 |  | Current phase 2 - 20th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29353 | 29352 | 72A8 | 2 |  | Current phase 2 - 21st harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29355 | 29354 | 72AA | 2 |  | Current phase 2 - 22nd harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29357 | 29356 | 72AC | 2 |  | Current phase 2 - 23rd harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29359 | 29358 | 72AE | 2 |  | Current phase 2 - 24th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29361 | 29360 | 72B0 | 2 |  | Current phase 2 - 25th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29363 | 29362 | 72B2 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29365 | 29364 | 72B4 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29367 | 29366 | 72B6 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29369 | 29368 | 72B8 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29371 | 29370 | 72BA | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29373 | 29372 | 72BC | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29375 | 29374 | 72BE | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29377 | 29376 | 72C0 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29379 | 29378 | 72C2 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29381 | 29380 | 72C4 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29383 | 29382 | 72C6 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29385 | 29384 | 72C8 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29387 | 29386 | 72CA | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29389 | 29388 | 72CC | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29391 | 29390 | 72CE | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29393 | 29392 | 72D0 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29395 | 29394 | 72D2 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29397 | 29396 | 72D4 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29399 | 29398 | 72D6 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29401 | 29400 | 72D8 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29403 | 29402 | 72DA | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29405 | 29404 | 72DC | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29407 | 29406 | 72DE | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29409 | 29408 | 72E0 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29411 | 29410 | 72E2 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29441 | 29440 | 7300 | 200
29441 | 29440 | 7300 | 2 |  | Current phase 3 - 1st harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29443 | 29442 | 7302 | 2 |  | Current phase 3 - 2nd harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29445 | 29444 | 7304 | 2 |  | Current phase 3 - 3rd harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29447 | 29446 | 7306 | 2 |  | Current phase 3 - 4th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29449 | 29448 | 7308 | 2 |  | Current phase 3 - 5th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29451 | 29450 | 730A | 2 |  | Current phase 3 - 6th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29453 | 29452 | 730C | 2 |  | Current phase 3 - 7th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29455 | 29454 | 730E | 2 |  | Current phase 3 - 8th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29457 | 29456 | 7310 | 2 |  | Current phase 3 - 9th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29459 | 29458 | 7312 | 2 |  | Current phase 3 - 10th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29461 | 29460 | 7314 | 2 |  | Current phase 3 - 11th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29463 | 29462 | 7316 | 2 |  | Current phase 3 - 12th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29465 | 29464 | 7318 | 2 |  | Current phase 3 - 13th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29467 | 29466 | 731A | 2 |  | Current phase 3 - 14th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29469 | 29468 | 731C | 2 |  | Current phase 3 - 15th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29471 | 29470 | 731E | 2 |  | Current phase 3 - 16th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29473 | 29472 | 7320 | 2 |  | Current phase 3 - 17th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29475 | 29474 | 7322 | 2 |  | Current phase 3 - 18th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29477 | 29476 | 7324 | 2 |  | Current phase 3 - 19th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29479 | 29478 | 7326 | 2 |  | Current phase 3 - 20th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29481 | 29480 | 7328 | 2 |  | Current phase 3 - 21st harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29483 | 29482 | 732A | 2 |  | Current phase 3 - 22nd harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29485 | 29484 | 732C | 2 |  | Current phase 3 - 23rd harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29487 | 29486 | 732E | 2 |  | Current phase 3 - 24th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29489 | 29488 | 7330 | 2 |  | Current phase 3 - 25th harmonic (rms) | unsigned integer | 1 | mA |  |  | 3
29491 | 29490 | 7332 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29493 | 29492 | 7334 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29495 | 29494 | 7336 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29497 | 29496 | 7338 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29499 | 29498 | 733A | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29501 | 29500 | 733C | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29503 | 29502 | 733E | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29505 | 29504 | 7340 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29507 | 29506 | 7342 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29509 | 29508 | 7344 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29511 | 29510 | 7346 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29513 | 29512 | 7348 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29515 | 29514 | 734A | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29517 | 29516 | 734C | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29519 | 29518 | 734E | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29521 | 29520 | 7350 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29523 | 29522 | 7352 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29525 | 29524 | 7354 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29527 | 29526 | 7356 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29529 | 29528 | 7358 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29531 | 29530 | 735A | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29533 | 29532 | 735C | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29535 | 29534 | 735E | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29537 | 29536 | 7360 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29539 | 29538 | 7362 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29569 | 29568 | 7380 | 2 |  | Voltage phase 1 - 1st harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29571 | 29570 | 7382 | 2 |  | Voltage phase 1 - 2nd harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29573 | 29572 | 7384 | 2 |  | Voltage phase 1 - 3rd harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29575 | 29574 | 7386 | 2 |  | Voltage phase 1 - 4th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29577 | 29576 | 7388 | 2 |  | Voltage phase 1 - 5th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29579 | 29578 | 738A | 2 |  | Voltage phase 1 - 6th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29581 | 29580 | 738C | 2 |  | Voltage phase 1 - 7th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29583 | 29582 | 738E | 2 |  | Voltage phase 1 - 8th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29585 | 29584 | 7390 | 2 |  | Voltage phase 1 - 9th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29587 | 29586 | 7392 | 2 |  | Voltage phase 1 - 10th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29589 | 29588 | 7394 | 2 |  | Voltage phase 1 - 11th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29591 | 29590 | 7396 | 2 |  | Voltage phase 1 - 12th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29593 | 29592 | 7398 | 2 |  | Voltage phase 1 - 13th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29595 | 29594 | 739A | 2 |  | Voltage phase 1 - 14th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29597 | 29596 | 739C | 2 |  | Voltage phase 1 - 15th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29599 | 29598 | 739E | 2 |  | Voltage phase 1 - 16th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29601 | 29600 | 73A0 | 2 |  | Voltage phase 1 - 17th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29603 | 29602 | 73A2 | 2 |  | Voltage phase 1 - 18th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29605 | 29604 | 73A4 | 2 |  | Voltage phase 1 - 19th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29607 | 29606 | 73A6 | 2 |  | Voltage phase 1 - 20th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29609 | 29608 | 73A8 | 2 |  | Voltage phase 1 - 21st harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29611 | 29610 | 73AA | 2 |  | Voltage phase 1 - 22nd harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29613 | 29612 | 73AC | 2 |  | Voltage phase 1 - 23rd harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29615 | 29614 | 73AE | 2 |  | Voltage phase 1 - 24th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29617 | 29616 | 73B0 | 2 |  | Voltage phase 1 - 25th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29619 | 29618 | 73B2 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29621 | 29620 | 73B4 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29623 | 29622 | 73B6 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29625 | 29624 | 73B8 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29627 | 29626 | 73BA | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29629 | 29628 | 73BC | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29631 | 29630 | 73BE | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29633 | 29632 | 73C0 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29635 | 29634 | 73C2 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29637 | 29636 | 73C4 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29639 | 29638 | 73C6 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29641 | 29640 | 73C8 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29643 | 29642 | 73CA | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29645 | 29644 | 73CC | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29647 | 29646 | 73CE | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29649 | 29648 | 73D0 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29651 | 29650 | 73D2 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29653 | 29652 | 73D4 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29655 | 29654 | 73D6 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29657 | 29656 | 73D8 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29659 | 29658 | 73DA | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29661 | 29660 | 73DC | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29663 | 29662 | 73DE | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29665 | 29664 | 73E0 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29667 | 29666 | 73E2 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29697 | 29696 | 7400 | 200
29697 | 29696 | 7400 | 2 |  | Voltage phase 2 - 1st harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29699 | 29698 | 7402 | 2 |  | Voltage phase 2 - 2nd harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29701 | 29700 | 7404 | 2 |  | Voltage phase 2 - 3rd harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29703 | 29702 | 7406 | 2 |  | Voltage phase 2 - 4th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29705 | 29704 | 7408 | 2 |  | Voltage phase 2 - 5th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29707 | 29706 | 740A | 2 |  | Voltage phase 2 - 6th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29709 | 29708 | 740C | 2 |  | Voltage phase 2 - 7th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29711 | 29710 | 740E | 2 |  | Voltage phase 2 - 8th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29713 | 29712 | 7410 | 2 |  | Voltage phase 2 - 9th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29715 | 29714 | 7412 | 2 |  | Voltage phase 2 - 10th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29717 | 29716 | 7414 | 2 |  | Voltage phase 2 - 11th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29719 | 29718 | 7416 | 2 |  | Voltage phase 2 - 12th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29721 | 29720 | 7418 | 2 |  | Voltage phase 2 - 13th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29723 | 29722 | 741A | 2 |  | Voltage phase 2 - 14th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29725 | 29724 | 741C | 2 |  | Voltage phase 2 - 15th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29727 | 29726 | 741E | 2 |  | Voltage phase 2 - 16th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29729 | 29728 | 7420 | 2 |  | Voltage phase 2 - 17th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29731 | 29730 | 7422 | 2 |  | Voltage phase 2 - 18th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29733 | 29732 | 7424 | 2 |  | Voltage phase 2 - 19th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29735 | 29734 | 7426 | 2 |  | Voltage phase 2 - 20th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29737 | 29736 | 7428 | 2 |  | Voltage phase 2 - 21st harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29739 | 29738 | 742A | 2 |  | Voltage phase 2 - 22nd harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29741 | 29740 | 742C | 2 |  | Voltage phase 2 - 23rd harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29743 | 29742 | 742E | 2 |  | Voltage phase 2 - 24th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29745 | 29744 | 7430 | 2 |  | Voltage phase 2 - 25th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29747 | 29746 | 7432 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29749 | 29748 | 7434 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29751 | 29750 | 7436 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29753 | 29752 | 7438 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29755 | 29754 | 743A | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29757 | 29756 | 743C | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29759 | 29758 | 743E | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29761 | 29760 | 7440 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29763 | 29762 | 7442 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29765 | 29764 | 7444 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29767 | 29766 | 7446 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29769 | 29768 | 7448 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29771 | 29770 | 744A | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29773 | 29772 | 744C | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29775 | 29774 | 744E | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29777 | 29776 | 7450 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29779 | 29778 | 7452 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29781 | 29780 | 7454 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29783 | 29782 | 7456 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29785 | 29784 | 7458 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29787 | 29786 | 745A | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29789 | 29788 | 745C | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29791 | 29790 | 745E | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29793 | 29792 | 7460 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29795 | 29794 | 7462 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29825 | 29824 | 7480 | 2 |  | Voltage phase 3 - 1st harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29827 | 29826 | 7482 | 2 |  | Voltage phase 3 - 2nd harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29829 | 29828 | 7484 | 2 |  | Voltage phase 3 - 3rd harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29831 | 29830 | 7486 | 2 |  | Voltage phase 3 - 4th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29833 | 29832 | 7488 | 2 |  | Voltage phase 3 - 5th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29835 | 29834 | 748A | 2 |  | Voltage phase 3 - 6th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29837 | 29836 | 748C | 2 |  | Voltage phase 3 - 7th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29839 | 29838 | 748E | 2 |  | Voltage phase 3 - 8th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29841 | 29840 | 7490 | 2 |  | Voltage phase 3 - 9th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29843 | 29842 | 7492 | 2 |  | Voltage phase 3 - 10th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29845 | 29844 | 7494 | 2 |  | Voltage phase 3 - 11th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29847 | 29846 | 7496 | 2 |  | Voltage phase 3 - 12th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29849 | 29848 | 7498 | 2 |  | Voltage phase 3 - 13th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29851 | 29850 | 749A | 2 |  | Voltage phase 3 - 14th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29853 | 29852 | 749C | 2 |  | Voltage phase 3 - 15th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29855 | 29854 | 749E | 2 |  | Voltage phase 3 - 16th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29857 | 29856 | 74A0 | 2 |  | Voltage phase 3 - 17th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29859 | 29858 | 74A2 | 2 |  | Voltage phase 3 - 18th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29861 | 29860 | 74A4 | 2 |  | Voltage phase 3 - 19th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29863 | 29862 | 74A6 | 2 |  | Voltage phase 3 - 20th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29865 | 29864 | 74A8 | 2 |  | Voltage phase 3 - 21st harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29867 | 29866 | 74AA | 2 |  | Voltage phase 3 - 22nd harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29869 | 29868 | 74AC | 2 |  | Voltage phase 3 - 23rd harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29871 | 29870 | 74AE | 2 |  | Voltage phase 3 - 24th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29873 | 29872 | 74B0 | 2 |  | Voltage phase 3 - 25th harmonic (rms) | unsigned integer | 1 | mV |  | See Note 4 | 3
29875 | 29874 | 74B2 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29877 | 29876 | 74B4 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29879 | 29878 | 74B6 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29881 | 29880 | 74B8 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29883 | 29882 | 74BA | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29885 | 29884 | 74BC | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29887 | 29886 | 74BE | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29889 | 29888 | 74C0 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29891 | 29890 | 74C2 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29893 | 29892 | 74C4 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29895 | 29894 | 74C6 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29897 | 29896 | 74C8 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29899 | 29898 | 74CA | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29901 | 29900 | 74CC | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29903 | 29902 | 74CE | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29905 | 29904 | 74D0 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29907 | 29906 | 74D2 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29909 | 29908 | 74D4 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29911 | 29910 | 74D6 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29913 | 29912 | 74D8 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29915 | 29914 | 74DA | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29917 | 29916 | 74DC | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29919 | 29918 | 74DE | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29921 | 29920 | 74E0 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
29923 | 29922 | 74E2 | 2 |  | RESERVED (returns 0000 0000h) | [5 empty] | 3
DETAILS
[5 empty] | Note 1 | Type | Scale | Unit | Range | Condition
[7 empty] | 0.01 | W, var, VA |  | CTxVT<5.000
[7 empty] | 1 | W, var, VA |  | CTxVT ≥ 5.000
[5 empty] | Note 2 | Type | Scale | Unit | Range | Condition
[7 empty] | 1.000.000 | Wh, varh |  | 100.000 ≤ CTxVT < 1.000.000
[7 empty] | 100.000 | Wh, varh |  | 10.000 ≤ CTxVT < 100.000
[7 empty] | 10.000 | Wh, varh |  | 1.000 ≤ CTxVT < 10.000
[7 empty] | 1.000 | Wh, varh |  | 100 ≤ CTxVT < 1.000
[7 empty] | 100 | Wh, varh |  | 10 ≤ CTxVT < 100
[7 empty] | 10 | Wh, varh |  | 1 ≤ CTxVT < 10
TARIFFS
[5 empty] | Note 3 | Inputs status |  | Tariff
[6 empty] | 0x00: In1 Open, In2 Open |  | Tariff 1
[6 empty] | 0x01: In1 Close, In2 Open |  | Tariff 2
[6 empty] | 0x02: In1 Open, In2 Close |  | Tariff 3
[6 empty] | 0x03: In1 Close, In2 Close |  | Tariff 4
VOLTAGE THD, HARMONICS AND STATISTICS
[5 empty] | Note 4 | Network Type
[6 empty] | With Neutral |  | data related to phase voltages
[6 empty] | Without Neutral |  | data related to chained voltages

## HOLDING REGISTERS - Words (R&W)
Register Number | Register Address (Dec) | Register Address (Hex) | Dimension [word] | Bit Position | Description | Type | Scale | Unit | Range | Note | Read Function Codes (Dec) | Write Function Codes (Hex) | Data Storing (2)
257 | 256 | 100 | 2 |  | Current & Voltage Transf. Ratio
257 | 256 | 100 | 1 |  | Write Current transformer ratio - CT | unsigned integer | 1 | - | 1 ÷ 9999 | CT = I prim / I sec ex: 500 A / 5 A ® CT = 100 | 3 | 10
259 | 258 | 102 | 1 |  | Write Voltage transformer ratio - VT | unsigned integer | 0.01 | - | 100 ÷ 1000 | VT = V prim / V sec ex: 600 V /100 V VT = 6.00 ® WRITE 600 --- If tranformer not present VT = 1.00 ® WRITE 100 | 3 | 10
260 | 259 | 103 | 1 |  | Energy mode accumulation | unsigned integer | - | - | 0, 1, 2, 3 | 0: Asyn 1: Syn 2: Tariff 3: Pulse Counting | 3 | 10
4208 | 4207 | 106F | 31 |  | Output Remote Command
4208 | 4207 | 106F | 1 |  | Output Remote Command | unsigned integer | - | - | 0, 1, | 0: Deactivate 1: Activate | - | 10
8193 | 8192 | 2000 | 16 |  | Standard Setup parameters (write 16 byte at once)
8193 | 8192 | 2000 | 1 |  | RESERVED (returns 0000h)
8194 | 8193 | 2001 | 1 |  | RESERVED (returns 0000h)
8195 | 8194 | 2002 | 1 |  | RESERVED (returns 0000h)
8196 | 8195 | 2003 | 1 |  | RESERVED (returns 0000h)
8197 | 8196 | 2004 | 1 |  | Percentage of rated 3phase active power run hour meter | unsigned integer | 0.01 | % | 50 ÷ 5000 | 50 ÷ 5000 means (0.5% ÷ 50.00%) | 3 | 10
8198 | 8197 | 2005 | 1 |  | Run hour meter active on | unsigned integer | - | - | 0, 1 | 0: Voltages, 1 Power | 3 | 10
8199 | 8198 | 2006 | 1 |  | RESERVED (returns 0000h)
8200 | 8199 | 2007 | 1 |  | RESERVED (returns 0000h)
8201 | 8200 | 2008 | 1 |  | Backlight intensity | unsigned integer | - | - | 0, 1, 2, 3 | 0: 0% 1: 35% 2: 70% 3: 100% | 3 | 10
8202 | 8201 | 2009 | 1 |  | RESERVED (returns 0000h)
8203 | 8202 | 200A | 1 |  | Power Averaging time | unsigned integer | - | - | 0, 1, 2, 3, 4, 5, 6 | 0: 5min 1: 8min 2: 10min 3: 15min 4: 20min 5: 30min 6: 60min | 3 | 10
8204 | 8203 | 200B | 1 |  | Insertion type | unsigned integer | - | - | 0, 1, 2, 3, 4, 5 | 0: 3N-3E 1: 3-3E 2: 3-2E 3: 1N-1E 4: 3N-1E 5: 3-1E | 3 | 10
8205 | 8204 | 200C | 1 |  | Measure on line 1 of custom page | unsigned integer | - | - | 0 ÷ 10 | 0:V1 1:V12 2:I1 3:In 4:P 5:Q 6:S 7:P1 8:Q1 9:S1 10:PF 3-phase | 3 | 10
8206 | 8205 | 200D | 1 |  | Measure on line 2 of custom page | unsigned integer | - | - | 0 ÷ 10 | 0:V2 1:V23 2:I2 3:P 4:Q 5:S 6:P2 7:Q2 8:S2 9:Freq 10:I1 | 3 | 10
8207 | 8206 | 200E | 1 |  | Measure on line 3 of custom page | unsigned integer | - | - | 0 ÷ 10 | 0:V3 1:V31 2:I3 3:P 4:Q 5:S 6:P3 7:Q3 8:S3 9:P1 10:I1 | 3 | 10
8208 | 8207 | 200F | 1 |  | RESERVED (returns 0000h)
8705 | 8704 | 2200 | 24 |  | Output option Setup parameters (write 24 byte at once)
8705 | 8704 | 2200 | 1 | W0 | RESERVED (returns 0000h)
8706 | 8705 | 2201 | 1 | W1 | RESERVED (returns 0000h)
8707 | 8706 | 2202 | 1 | W2 | RESERVED (returns 0000h)
8708 | 8707 | 2203 | 1 | W3 | RESERVED (returns 0000h)
8709 | 8708 | 2204 | 1 | W4 | RESERVED (returns 0000h)
8710 | 8709 | 2205 | 1 | W5 | RESERVED (returns 0000h)
8711 | 8710 | 2206 | 1 | W6 | RESERVED (returns 0000h)
8712 | 8711 | 2207 | 1 | W7 | RESERVED (returns 0000h)
8713 | 8712 | 2208 | 1 | W8 | RESERVED (returns 0000h)
8714 | 8713 | 2209 | 1 | W9 | RESERVED (returns 0000h)
8715 | 8714 | 220A | 1 | W10 | Output type | unsigned integer | - | - | 0, 1, 2, 3 | 0: Pulse out 1: Alarm out 2: Dual stable Remote command 3: Timed Remote command | 3 | 10
8716 | 8715 | 220B | 1 | W11 | Pulse duration | unsigned integer | - | - | 0, 1, 2, 3, 4, 5 | 0: 50 ms 1: 100 ms 2: 200 ms 3: 300 ms 4: 400 ms 5: 500ms | 3 | 10
8717 | 8716 | 220C | 1 | W12 | Pulse weight | unsigned integer | - | - | 0, 1, 2, 3, 4, 5, 6 | 0: 0.01 kWh 1: 0.10 kWh 2: 1.00 kWh 3: 10.0 kWh 4: 0.10 MWh 5: 1.00 MWh 6: 10.0 MWh | 3 | 10
8718 | 8717 | 220D | 1 | W13 | Pulse active on | unsigned integer | - | - | 0, 1 | 0: Active Energy 1: Reactive Energy | 3 | 10
8719 | 8718 | 220E | 1 | W14 | Alarm deactivation delay or Relay closing time (if Output type = Timed Remote command) | unsigned integer | 1 | s | 0 ÷ 99 | - | 3 | 10
8720 | 8719 | 220F | 1 | W15 | Alarm activation delay | unsigned integer | 1 | s | 0 ÷ 99 | - | 3 | 10
8721 | 8720 | 2210 | 1 | W16 | Hysteresis | unsigned integer | 1 | % | 0 ÷ 20 | - | 3 | 10
8722 | 8721 | 2211 | 1 | W17 | Relay (NO/NC) | unsigned integer | - | - | 0, 1 | 0: NO 1: NC | 3 | 10
8723 | 8722 | 2212 | 1 | W18 | Alarm on Min Value or Max Value | unsigned integer | - | - | 0, 1 | 0: Min 1: Max | 3 | 10
8724 | 8723 | 2213 | 1 | W19 | Alarm setpoint | unsigned integer | - | - | 0 ÷ 9999 | - | 3 | 10
8725 | 8724 | 2214 | 1 | W20 | RESERVED (returns 0000h)
8726 | 8725 | 2215 | 1 | W21 | Unit of setpoint | unsigned integer | - | - | 0, 1, 2, 3, 4, 5, 6, 7, 8 | 0: X.XXX 1: XX.XX 2: XXX.X 3: X.XXX k 4: XX.XX k 5: XXX.X k 6: X.XXX M 7: XX.XX M 8: XXX.X M | 3 | 10
8727 | 8726 | 2216 | 1 | W22 | Sign of Alarm setpoint (Only for Energies) | unsigned integer | - | - | 0, 1 | 0: "+" 1: "-" | 3 | 10
8728 | 8727 | 2217 | 1 | W23 | Type of measure | unsigned integer |  |  |  | 0:V1 1:V2 2:V3 3:V12 4:V23 5:V31 6:I1 7:I2 8:I3 9:Freq 10:Active Power 11:Reactive Power | 3 | 10
9217 | 9216 | 2400 | 1 |  | Reset parameters
9217 | 9216 | 2400 | 1 |  | Reset Hour Meter, Maximum Powers, Maximum Voltages, Maximum Currents, Minimum Voltages, Active Partial Energy, Reactive Partial Energy | unsigned integer | - | - | - | See Note 1
9729 | 9728 | 2600 | 1 |  | Saving parameters
9729 | 9728 | 2600 | 1 |  | Saving in EEPROM parameters changed by Remote commands | unsigned integer | - | - | - | See Note 2 | 3 | 10
9985 | 9984 | 2700 | 1 |  | Enable writing
9985 | 9984 | 2700 | 1 |  | Enable Remote Writing Operation | unsigned integer | - | - | - | See Note 2 & Note 3 | 3 | 10
10241 | 10240 | 2800 | 1 |  | Restore default parameters
10241 | 10240 | 2800 | 1 |  | Restore default parameters | unsigned integer | - | - | - | See Note 3 | 3 | 10
Note 1 - Reset parameters
To reset desired measurements write the following word (in binary): 0¦0¦0¦0¦0¦0¦0¦0¦b8¦b7¦b6¦b5¦b4¦b3¦b2¦b1¦b0 b0 = 1 => Reset Hour Meter b1 = 1 => Reset Peak Maximum Demand b2 = 1 => Reset Maximum Voltage values b3 = 1 => Reset Maximum Current values b4 = 1 => Reset Minimum Voltage values b5 = 1 => Reset Active Partial Energy b6 = 1 => Reset Reactive Partial Energy b7 = 1 => Reset Counter Input 1 ( Sw > 1.02 ) b8 = 1 => Reset Counter Input 2 ( Sw > 1.02 ) b9 ÷ b15 = 0
Note 2 - Configuration Procedure
1) "Master Unlock Key” command (write the value = 0x5AA5 in the register 0x2700)
2) Write the new Configuration (one or more registers...)
3) "Master Unlock Key” command (write the value = 0x5AA5 in the register 0x2700)
4) Save/Confirm the new Configuration (writing the value 0x000A in the register 0x2600)
5) The new Configuration is now available
Note 3 - Restore default parameters
1) "Master Unlock Key” command (write the value = 0x5AA5 in the register 0x2700)
3) Return to the Default configuration (writing the value 0x000B in the register 0x2800)
4) The Default configuration has been restored